1. Heat leak
  1. Normally Open valve (i.e. open if mains fails)
  2. Pipe thermostat
    1. for over-temperature (> 95ºC)
    2. Could also turn on pump(s)
2. Woodburner Pump.
  1. Has 10mm bypass for permanent cold feed (Probably not needed)
  2. Operates if:
    1. Flue thermostat > 100ºC
3. Woodburner return loading valve ensures water back to woodburner is over 61ºC
4. Oil Boiler Pump.
  1. Pump turned OFF if
    1. TS_middle temperature > (DHWtemp+hysteresis) OR
    2. Woodburner supply temperature > TS_bottom temperature
  2. Pump turned ON if
    1. TS_bottom temperature < (DHWtemp-hysteresis) AND
    2. Woodburner supply temperature < TS_bottom temperature
5. Radiators/UFH Pump.
  1. Turned OFF if
    1. TS_top temperature < DHWmin (to keep DHW from being robbed)
  2. Turned ON if:
    1. Time clock & Thermostat OR
    2. Thermal Store overheat > 85ºC
6. Under Floor Pump(s).
  1. Includes mixer valve
  2. Operates if:
    1. Time clock & Thermostat OR
    2. Thermal Store overheat > 85ºC (should also ensure at least 1 zone valve is open)
7. Inputs
  1. Call for Heat (Radiators) - GPIO13
  2. Call for Heat (Underfloor House) - GPIO12
  3. Call for Heat (Underfloor extension) - GPIO14
  4. Thermal Store over temperature - GPIO16
8. Outputs
  1. Oil Boiler pump – GPIO04
  2. Heating Pump - GPIO05