Diagram Notes Boiler Controller
Hardware
The circuit diagram of the Boiler Controller is entitled Thermal Store CPU. This board has:
•
- Power supply (3.3V & 5V)
- ESP8266 (ESP-12) cpu with WiFi
- MCP2309 Input/Output extender
- 5 x 240V-5V power supplies that act as the interface to the mains signals
- A 4 way solid state relay to output mains control signals
- Interface to 6 x DS18B20 temperature sensors
- Reset, and User switches
Connector to allow software uploading and testing
Software
The software has a number of settings used to control how the BC operates:
Setting ID	E.g. values	Description
0 DHW Set Point	60	The target temperature for the Top of theTS
1 UFH Set Point	45	The temperature of the middle of the TS when the
UFH but not the Radiators are calling for heat at which heating (OB or WB) will be used
2 Rads Set Point	55	The temperature of the middle of the TS when the
Radiators are calling for heat at which heating (OB or WB) will be used
3 Set Point Differential	10	The additional temperature (to the set point) above
which the heating (OB) will be turned off
4 WB is ON Temp	65	The temperature above which it will be considered
that the WB is supplying heat
5 DHW Use all Heat	48	(Not currently used)
6 Outside Temperature	10	The amount the CH set point will be reduced when
Compensation	the Outside temperature is at or above the High
Point (currently 20C)
7 Boost Time	5	The time (in minutes) between checking whether a
heating boost is required when OTC is applicable
8 Boost Amount	2	The amount the CH set point will be increased each
Boost Time if the CH is still calling for heat
9 Emergency Dump	95	The TS Top temperature above which the
temperature	Emergency Heat Dump signal will be operated.
(currently set to operate the Dining Room UFH)
10 OB Pump ON delay	10	The time (in seconds) by which the OB circulation
pump is delayed when the OB is turned on.
11 DHW ON Hour	7	The time from which DHW is required
12 DHW OFF Hour	22	The time from which DHW is no longer required